CHAPTER 100

WASTEWATER TREATMENT PONDS (LAGOONS)

100.	GENERAL

This Chapter deals with generally used variations of treatment ponds to achieve secondary treatment including controlled-discharge, flow-through and aerated pond systems.

101.	SUPPLEMENT TO ENGINEER'S REPORT

The engineer's report shall contain pertinent information on location, geology, soil conditions, area for expansion and any other factors that will affect the feasibility and acceptability of the proposed project.  The following information must be submitted in addition to that required in Chapter 10.

101.1	Supplementary Field Survey Data

101.1.1	Location of Nearby Facilities

The location and direction of all residential areas, commercial developments, parks, and recreational areas shall be included in the engineer's report.

101.1.2	Site Description

A description, including maps showing elevations and contours of the site and adjacent area shall be provided.  Due consideration shall be given to additional treatment units and/or increased waste loadings in determining land requirements.

101.1.3	Location of Field Tile

The location, depth, and discharge point of any field tile in the immediate area of the proposed site shall be identified.

101.1.4	Soil/Groundwater Study

Considering the leakage requirement set forth in Section 104.2.2.1, a soil/groundwater evaluation must be included for newly constructed facilities and additions to such facilities already in place.  This does not apply to basins formed with fiberglass, concrete, etc., nor to existing earthen facilities not being enlarged or deepened.

101.1.4.1	Liner Proposed

Where a liner such as bentonite or synthetic material is proposed to meet the leakage limit, the soil/groundwater study may be limited to the following:

- A general review of the local geology, hydrology, and current and potential groundwater resources, including information from published literature (soil maps and cross sections, etc.), applicable files and databases at the USGS and MDEQ.

b.	A brief description of the proposed liner (material type, thickness, hydraulic conductivity, etc.).

c.	A statement that with the proposed liner the leakage limit will not be exceeded.

101.1.4.2	Liner Determined Unnecessary

Where a liner is determined in the report to be unnecessary to meet the leakage limit due to the characteristics of in-situ material, the soil/groundwater study must include the following:

___	a.	The information listed in Section 101.1.4.1.a.

___	b.	A USGS topographic map (1:24,000 scale) with the project site and a one mile

radius area of review denoted.  The location and depth of all recorded water wells within the area of review must be shown.  An effort must be made to determine if residences within the area of review have private wells that may not be listed on Office of Land and Water Resources (OLWR) or USGS inventories

___	c.	Soil borings of sufficient depth and number to characterize the soil/groundwater

conditions below the planned excavation and to demonstrate that an in-situ competent liner is present.  These borings must be continuous and extend to a depth of 25 feet below the bottom of the impoundment.  Permeability tests (either lab or field) must be conducted on undisturbed samples taken from the interval that will serve as the natural liner.  ASTM procedures or acceptable similar methods should be followed for all tests.  The table below specifies the minimum number of borings and permeability tests based on impoundment size.

Impoundment Acreage	Minimum # Borings	Minimum # Perm. Tests

<10				 5			    3

>10 to 20			 7			    4

>20 to 30			10			    5

>30				15			    7

If a shallow aquifer is encountered, groundwater levels from at least 3 temporary piezometers must be monitored to determine flow direction and rate.

Boring logs and cross-sections showing thickness, lateral continuity, and lithology should be submitted as part of the study.

___	d.	Well drillers' logs (available from OLWR) and geophysical logs (available from

the USGS and the Office of Geology) for the water wells within the one-mile radius area of review.  Information to be included with the logs are identification number, location, date drilled, depth, use, pumping rate, casing size and screen length.

___	e.	A statement that given the documented conditions the leakage limit will not be

exceeded.

102.	LOCATION

102.1	Surface Runoff

Location of ponds in watersheds receiving significant amounts of stormwater runoff is discouraged.  Adequate provision must be made to divert stormwater runoff around the ponds and protect pond embankments from erosion.

102.2	Hydrology

Construction of ponds in close proximity to water supplies and other facilities subject to contamination should be avoided.  A minimum separation of 4 feet (1.2 m) between the bottom of the pond and the maximum groundwater elevation should be maintained.

102.3	Geology

A minimum separation of 10 feet (3.0 m) between the pond bottom and any bedrock formation is recommended.

103.	BASIS OF DESIGN

The maximum size of a lagoon cell should be 40 acres.

When there are multiple cells, the piping should allow individual cells to be isolated.

103.1	Facultative Lagoon

The system shall be designed with at least two cells in series.  The first cell shall be loaded no heavier than 40 lb BOD5/ac/d.  The overall loading shall be no heavier than 30 lb BOD5/ac/d.  Loadings shall be determined using the surface area at the 4 foot operating depth.

The minimum detention time shall be 30 days overall at the 4 foot operating depth.

103.2	Aerated Lagoon

103.2.1	Partially Mixed Aerated Lagoon

The minimum detention time of the aerated cell shall be 18 days.

There shall be a settling area with a minimum detention time of 1 day.  A separate settling cell is preferred.  The settling area may be a quiescent portion of the aerated cell, in which case the total detention time must be at least 19 days.

For mechanical aerators, a minimum aeration capacity of 8 hp per MG of aeration pond volume (at the 4 foot depth) should be provided.  This capacity is intended to provide oxygen for BOD conversion and a reasonable amount of energy for mixing.  Wastewater that is stronger than domestic wastewater may require more aeration capacity.

If less aeration capacity is provided, the aerators shall be able to continuously maintain a minimum DO level of 2 mg/1 in the top two feet of water and in the effluent.

103.2.2	Completely Mixed Aerated Lagoon

The aerators shall be able to completely mix the lagoon contents and to continuously maintain a minimum DO level of 2 mg/1 in all parts of the lagoon and in the effluent.

A settling area must be provided.  Either a separate settling cell with a 1 day detention time or a clarifier designed according to Chapter 60 may be used.

If the settling area will be a portion of the aerated cell, it must be separated with a baffle.

103.3	Hydrograph Controlled Release Lagoon

Single cell hydrograph controlled release (HCR) lagoon systems are not allowed.  The treatment portion of an HCR lagoon system may be (a) a lagoon designed according to Section 103.1 or 103.2, (b) a single-cell facultative lagoon loaded no heavier than 30 lb BOD5/ac/d, or (c) other methods for producing secondary effluent.

The minimum required storage time shall be 90 days, and 180 days is considered sufficient without further analysis.  Storage times between 90 and 180 days shall be determined by using procedures acceptable to the MDEQ/OPC/SWD/WQMS & TMDL Branch.  Excess detention time in the first cell of an HCR lagoon system shall not be counted toward the required storage time, but treatment and storage capacity can coexist in the second (and subsequent) cell(s).

103.4	Anaerobic Lagoon

Anaerobic lagoons may be used as pretreatment for high strength wastewaters with enough oil/grease to form a scum cover.  Anaerobic lagoons shall not be used for typical domestic wastewater unless there is some positive method of providing a cover or seal.

The lagoon shall be designed so that a complete scum cover can be maintained.  The surface area should be relatively small to prevent breakup of the cover by wind.  Anaerobic lagoons shall not be used where the influent flow fluctuates widely.

Loading should be 175 to 2000 lb BOD5/ac/d.

The minimum detention time should be 20 days.

103.5	Pretreatment Lagoon

Odor control methods should be included if the loading will exceed 50 lb BOD5/ac/d.

103.6	Pond Shape

The shape of all cells should be such that there are no narrow or elongated portions.  Round, square, or rectangular ponds with a length not exceeding three times the width are considered most desirable.  No islands, peninsulas or coves shall be permitted.  Dikes should be rounded at corners to minimize accumulations of floating materials.  Common-wall dike construction, wherever possible, is strongly encouraged.

104.	POND CONSTRUCTION DETAILS

104.1	Embankments and Dikes

104.1.1	Material

Dikes shall be constructed of structurally stable relatively impervious material and compacted to at least 90% Standard Proctor Density to form a stable structure.  Vegetation and other unsuitable materials shall be removed from the area where the embankment is to be placed.

104.1.2	Top Width

The minimum dike width shall be 8 ft (2.4 m) to allow access by maintenance vehicles.

104.1.3	Maximum Slopes

Earthen inner and outer dike slopes shall not be steeper than 3 horizontal to 1 vertical (3:1).  Paved or other protected slopes not requiring mowing, etc. should not be steeper than 2:1.

104.1.4	Minimum Slopes

Inner slopes should not be flatter than 4 horizontal to 1 vertical (4:1).  Flatter slopes can be specified for larger installations because of wave action but have the disadvantage of added shallow areas being conducive to emergent vegetation.  Outer slopes shall be sufficient to prevent surface runoff from entering the ponds.

104.1.5	Freeboard

Minimum freeboard shall be 3 feet (1.0 m).  For very small systems, 2 feet (0.6 m) may be acceptable.

104.1.6	Design Depth

The minimum operating depth of lagoons shall be not less than 4 feet; exceptions may be made for aerobic lagoons.

It should not be possible to drain the lagoon lower than the 2 foot level.  If shallower drainage is provided for, the drain shall be relatively inaccessible to prevent draining the pond by accident or vandalism.

104.1.6.1	Facultative Lagoon

The maximum operating depth shall be no more than 6 feet in primary cells.  Greater depths in subsequent cells are permissible although supplemental aeration or mixing may be necessary.

104.1.6.2	Aerated Lagoon

The design water depth of the aerated cell should be 10 to 15 feet.  Shallower depths may be used if the pond bottom is protected against scouring by the aerators.

The maximum operating depth of a separate settling cell shall be no more than 6 feet.

104.1.6.3	Hydrograph Controlled Release Lagoon

The maximum operating depth of a treatment/storage HCR cell should be no more than 15 feet.

The maximum operating depth of an HCR storage cell should be no more than 20 feet.

104.1.6.4	Anaerobic Lagoon

The design water depth should be 8 to 20 feet.

104.1.6.5	Pretreatment Lagoon

The design water depth should be 6 to 20 feet.

104.1.7	Erosion Control

Excessive erosion of the dikes must be prevented.

104.1.7.1	Seeding

The dikes shall have a cover layer of at least 4 inches (10 cm), of fertile topsoil to promote establishment of an adequate vegetative cover wherever other erosion control is not utilized.  Prior to prefilling (in accordance with 104.2.4), adequate vegetation shall be established on dikes from the outside toe to 2 feet (0.6 m) above the pond bottom on the interior as measured on the slope.  Perennial-type, low-growing, spreading grasses that minimize erosion and can be mowed are most satisfactory.  In general, alfalfa and other long-rooted crops should not be used since the roots of this type are apt to impair the water holding efficiency of the dikes.

104.1.7.2	Additional Erosion Protection

An acceptable method of erosion control is required as a minimum around all piping entrances and exists.  For aerated cells the design should ensure erosion protection on the slopes and bottoms in the areas where turbulence will occur.  Additional erosion control may also be necessary on the exterior dike slope to protect the embankment from erosion due to severe flooding of a watercourse.  Filter material should be used underneath any riprap.

104.1.7.3	Alternate Erosion Protection

Alternate erosion control on the interior dike slopes may be necessary for ponds that are subject to severe wave action.  In these cases erosion protection shall be placed from one foot (0.3 m) above the high water mark to two feet (0.6 m) below the low water mark (measured on the vertical).

If synthetic liners are used, some method shall be provided to allow people or animals that have fallen into the lagoon to climb out without having to swim too far.

104.2	Pond Bottom

104.2.1	Soil

Soil used in constructing the pond bottom (not including seal) and dike cores shall be relatively incompressible and tight and compacted at or up to 4% above the optimum water content to at least 90% Standard Proctor Density.

104.2.2	Seal

A seal or liner may be required in accordance with Section 101.1.4.

104.2.2.1	Leakage Limit

The water loss from each lagoon cell shall not exceed 500 gpd/ac at a head equal to the maximum operating depth of the cell.

104.2.2.2	Testing Requirements

The P/S shall include a requirement that the leakage limit be met and shall include a specific testing method.

If testing will be done by soil borings or other localized testing methods, at least one test per cell shall be done; more should be done as needed.  If any individual test fails to meet the leakage limit, the area of the cell represented by that test shall be reworked and retested.  Field tests should be corrected for evaporation and precipitation, as appropriate.

104.2.2.3	Applicability

The leakage requirement shall apply to all newly constructed or modified cells that will receive wastewater, regardless of the degree of treatment.

The leakage requirement will not normally apply to existing cells when the cell will receive minor modifications which will not enlarge or deepen the cell and where the soil is known to be relatively impermeable.

104.2.3	Uniformity

The pond bottom shall be as level as possible at all points.  Finished elevations shall not be more than 3 inches (7.5 cm) from the average elevation of the bottom.

104.2.4	Prefilling

Prefilling the pond should be considered in order to protect the liner, to prevent weed growth, to reduce odor, and to maintain moisture content of the seal.  The dikes must be completely prepared as described in Sections 104.1.7.1-2 before introduction of water.

104.3	Influent Lines

104.3.1	Material

Generally accepted material for underground sewer construction shall be used for the influent line to the pond.

104.3.2	Manhole

A manhole or vented cleanout wye shall be installed prior to entrance of the influent line into the primary cell and shall be located as close to the dike as topography permits.  Its invert shall be at least 6 inches (15 cm) above the maximum operating level of the pond and provide sufficient hydraulic head without surcharging the manhole.

104.3.3	Flow Distribution

Flow distribution structures shall be designed to effectively split hydraulic and organic loads proportionally to parallel primary cells.

104.3.4	Placement

Influent lines should be located along the bottom of the pond and shall have adequate seal below them.

104.3.5	Point of Discharge

All primary cells shall have individual influent lines that terminate at approximately the center of the cell so as to minimize short-circuiting.  Consideration should be given to multi-influent discharge points for primary cells of 20 acres (8 ha) or larger to enhance the distribution of wasteload in the cell.

All aerated cells shall have influent lines that distribute the load within the mixing zone of the aeration equipment.  Consideration of multiple inlets should be closely evaluated for any diffused aeration system.

104.3.6	Influent Discharge Apron

The influent line may discharge horizontally, directed away from nearby dikes, or vertically.  The discharge may be into a shallow, saucer-shaped, depression.

The discharge flow shall remain below the water surface.  The end of the discharge line shall rest on a suitable concrete apron large enough to prevent the terminal influent velocity at the end of the apron from causing soil erosion.

104.4	Control Structures and Interconnecting Piping

104.4.1	Structure

Where possible, facilities design shall consider the use of multi-purpose control structures to facilitate normal operational functions such as drawdown and flow distribution, flow and depth measurement, sampling, pumps for recirculation, chemical additions and mixing, and minimization of the number of construction sites within the dikes.

As a minimum, control structures shall be (a) accessible for maintenance and adjustment of controls; (b) adequately ventilated for safety and to minimize corrosion; (c) locked to discourage vandalism; (d) contain controls to permit water level and flow rate control, complete shutoff, and complete draining; (e) constructed of non-corrodible materials (metal-on-metal contact in controls should be of similar alloys to discourage electro-chemical reactions); and (f) located to minimize short-circuiting within the cell and avoid freezing and ice damage.

Recommended devices to regulate water level are valves, slide tubes or dual slide gates.  Regulators should be designed so that they can be preset to stop flows at any elevation.

104.4.2	Piping

All piping shall be of cast iron or other acceptable material.  The piping shall not be located within or below the seal.  Pipes should be anchored with adequate erosion control.

104.4.2.1	Drawdown Structure Piping

a.	Submerged Takeoffs

For ponds designed for shallow or variable depth operations, submerged takeoffs are	 recommended.  Intakes shall be located a minimum of 10 feet (3.0 m) from the toe of the dike and 2 feet (0.6 m) from the top of the seal, and shall employ vertical withdrawal.

b.	Multi-Level Takeoffs

For ponds that are designed deep enough to permit stratification of pond content, multiple takeoffs are recommended.  There shall be a minimum of three withdrawal pipes at different elevations.  The bottom pipe shall conform to submerged takeoffs.  The other should utilize horizontal entrance.  Adequate structural support shall be provided.

c.	Surface Takeoffs

Under constant discharge conditions and/or for relatively shallow ponds under warm weather conditions, surface overflow type withdrawal is recommended.  A baffle shall extend at least one foot below the water surface to prevent discharge of floating material.  The baffle shall be located to allow accurate flow measurement and to prevent excessive currents.

d.	Emergency Overflow

To prevent overtopping of dikes, emergency overflow should be provided.

104.4.2.2	Hydraulic Capacity

The hydraulic capacity for continuous discharge structures and piping shall allow for a minimum of 250% of the design flow of the system.

105.	MISCELLANEOUS

105.1	Fencing

The pond area shall be enclosed with an adequate fence to prevent entering of livestock and discourage trespassing.  Fencing should not obstruct vehicle traffic on top of the dike.  A vehicle access gate of sufficient width to accommodate mowing equipment shall be provided.  All access gates shall be provided with locks.

105.2	Access

An all-weather access road shall be provided to the site to allow year-round maintenance.

105.3	Warning Signs

Appropriate permanent signs shall be provided along the fence around the pond to designate the nature of the facility and warn against trespassing.  At least one sign shall be provided on each side of the site and one for every 500 feet (150 m) of its perimeter.

105.4	Flow Measurement

Flow measurement requirements are presented in Section 46.6.  Effective weather protection shall be provided for the recording equipment.

105.5	Groundwater Monitoring

An approved system of wells or lysimeters may be required around the perimeter of the pond site to facilitate groundwater monitoring.  The need for such monitoring will be determined on a case-by-case basis.

105.6	Laboratory Equipment

For laboratory equipment refer to Chapter 40.

105.7	Pond Level Gauges

Pond level gauges shall be provided.